BUILDMEP.COM  |  FREE TEMPLATE

FCU Controls Handover Record and Maintenance Log

For fan coil units operated from a BMS touch panel or local room thermostat

This template covers the controls side of an FCU handover: the operator interface, the room thermostat, the controller, and the records a facilities team needs before it takes the system over. It does not cover FCU mechanical servicing, coil cleaning, filter replacement or valve maintenance, which belong in the equipment manuals.

Replace the bracketed placeholders with your own project information. Nothing in this template establishes approved operating limits, test values or warranty terms; those come from your commissioning records, your specification and your supplier agreement.

## How to use it

- Part 1 is a reading guide for the panel. Give it to operators before they touch a live unit.

- Part 2 and Part 3 are completed by the contractor and controls specialist before the final O&M issue.

- Part 4 records who to call. Part 5 is the running service log.

- Keep detailed functional test results in your site maintenance system; this log is the index to them.

# Part 1  Reading the panel: command against status

Most false fault calls on an FCU panel come from reading one field and assuming it proves another. A command field is what someone asked the unit to do. A status field is what the panel reports happened. They are separate points, they update at different times, and either can be a software state rather than physical feedback.

| Displayed field | What it tells you | What it does not tell you |
| --- | --- | --- |
| UNIT RUN/STOP COMMAND | The requested run state of the unit. | That the fan is actually turning, or that electrical power has been removed. This is not an isolation point. |
| FAN SPEED CONTROL | The speed that has been selected. | The speed the fan is running at. Read FAN SPEED STATUS as well. |
| FAN SPEED STATUS | The speed the panel reports. | Whether that figure is measured feedback or a software state. Confirm which in the commissioned point schedule. |
| FAN OPERATING MODE | Whether the unit is in AUTO or MANUAL. | The speed selection, which is a separate field and does not follow a mode change. |
| TEMP SETPOINT FROM HMI | The value typed at the panel. | That the unit is controlling to it yet. |
| CURRENT SET POINT | The setpoint the unit is actually controlling to. | Whether a local thermostat or central command can still override it. |
| CHW VALVE STATUS (%) | A valve command or position indication. | That chilled water is flowing, or that cooling is being delivered. |
| SPACE TEMPERATURE | The reading from the configured sensor. | Sensor accuracy or calibration date. Those sit in the commissioning records. |

## Three checks worth making a habit

- After any change, re-read both the command field and the matching status field once the normal site response time has passed. A command on its own proves nothing.

- After entering a setpoint, confirm the active setpoint has moved. Entry confirmation is not the same as a changed control value.

- Never judge whether a fan has stopped from a speed label. Use the run/stop command, the valve indication and the summary row together.

Persistent disagreement between a command and its status is a condition to record and refer, not something to correct by sending the command again.

# Part 2  Controls equipment register

Complete one line per device type. Attach the full asset list where the installation is large.

| Equipment | Manufacturer and model | Serial / tag | Quantity and location |
| --- | --- | --- | --- |
| Operator panel / HMI |  |  |  |
| System controller |  |  |  |
| Room thermostats |  |  |  |
| Network / gateway device |  |  |  |

## Control arrangement

Network protocol: [ ______________________ ]   Addressing scheme: [ ______________________ ]

Point mapping document reference: [ ______________________ ]

Command priority between panel, thermostat and central command: [ ______________________ ]

Do not infer the installed topology from a product catalogue. Record what is actually installed.

# Part 3  Handover record

Complete before the final O&M issue. Each line is a record the facilities team will need the first time something goes wrong.

| Required record | Status |
| --- | --- |
| Installed panel/HMI model, serial number, location and quantity |  |
| Installed controller model, panel tag, serial number and quantity |  |
| Thermostat variants, FCU mapping, supply and configured application |  |
| Complete FCU asset list with room or area names |  |
| As built panel wiring and controls network drawings |  |
| Network protocol, addressing and point schedule |  |
| Approved sequence of operation and command priority |  |
| Approved temperature range and normal operating settings |  |
| Statement of which status points are physical feedback and which are software states |  |
| Interlocks, alarm list, schedule and recovery procedure |  |
| Commissioning and functional test results |  |
| Site verification of stop-to-run and operator training record |  |
| Panel and controller backups, thermostat parameter record |  |
| Manufacturer operating and service instructions |  |
| Warranty certificate, spares register and service contacts |  |
| Agreed maintenance intervals and log location |  |

# Part 4  Support contacts and acceptance

| Role | Name, company, telephone and email |
| --- | --- |
| Controls supplier / service contact |  |
| Facilities contact |  |
| Emergency maintenance contact |  |
| Warranty claims contact |  |

## Acceptance

Verified by contractor: ______________________________    Date: ______________

Verified by controls specialist: __________________________    Date: ______________

Reviewed by consultant: _____________________________    Date: ______________

Accepted by facilities: ______________________________    Date: ______________

# Part 5  Maintenance and fault log

Record the mode, command and readings before and after any work. Identify every temporary override and confirm whether it was removed or approved to remain.

| Date | FCU tag | Inspection or fault | Action and verification | Technician |
| --- | --- | --- | --- | --- |

Free template from buildmep.com. Use it, edit it, put your own company details on it. Preliminary record-keeping aid only; it does not replace your project specification, commissioning records or the manufacturer instructions for the installed equipment.