## Calc
Fire Pump Head Calculator
BuildMEP.com ¦ Hazen-Williams, equivalent-length fittings, velocity checks, NFPA 20 curve check. Yellow cells are inputs.
Units | US
System demand
Design flow | 750 |  |  | Metric example: 2839 L/min, 6.9 bar, 9 m, 0.3 bar, 1.5 m, round 0.5 bar, limits 6 / 4.5 m/s
Residual pressure at remote point | 100
Elevation, pump discharge to highest point | 30
Other losses (backflow, alarm valve, meter) | 5
Suction: water above pump (+) / lift (−) | 5
Safety margin | 0 | %
Round pump pressure up to | 10
Velocity limit, discharge | 20
Velocity limit, suction | 15
Pipe segments (suction S and discharge D, in series). Leave Flow blank to use design flow. Length/flow in the units chosen above.
Velocity unit follows Units; fitting counts are numbers of each fitting.
Segment | Type | Size | Sch | Length | Flow (opt.) | C | 90° elbow (std) | 90° elbow (long) | 45° elbow | Tee (run) | Tee/cross (branch) | Gate valve | Butterfly valve | Swing check | ID (in) | Flow (gpm) | Velocity | Friction (psi/ft) | Fittings eq. (ft) | Loss (psi) | Velocity check
Suction line | S | 8" | 40 | 20 |  | 120 | 1 |  |  |  |  | 1
Pump room header | D | 8" | 40 | 160 |  | 120 | 2 |  |  |  | 1 | 1 |  | 1
Riser feed main | D | 6" | 40 | 300 |  | 120 | 3 | 2 |  |  |  | 1
Equivalent lengths for fittings with no listed value for that size are counted as zero (see Data sheet).
Result
Residual pressure at remote point
Static head (elevation)
Friction loss, discharge pipe and fittings
Other losses
Required discharge pressure
Available suction pressure (static − suction friction)
Net pump pressure required
With safety margin
Design net pressure (rounded up)
Pump rating (next standard flow)
Velocity checks
Pump curve check (NFPA 20) - enter the selected pump's values
Rated net pressure
Shutoff (churn) pressure
Pressure at 150% rated flow
Shutoff ≤ 140% of rated
Pressure at 150% flow ≥ 65% of rated
Rated pressure ≥ design net pressure
Disclaimer: free educational tool by BuildMEP.com. Method: P = 4.52 Q^1.85 / (C^1.85 d^4.87) psi/ft (NFPA 13) using actual pipe internal diameter. Verify tables, limits and results against the NFPA edition adopted on your project; not a substitute for a licensed engineer's review.

## Data
Pipe data (internal diameter, in) | [9 empty] | Standard rated flows (gpm) | Unit factors (driven by Units cell on Calc)
Nominal | DN | ID Sch 40 (in) | ID Sch 10 (in) | [6 empty] | 25 | Flow → gpm
1" | 25 | 1.049 | 1.097 | [6 empty] | 50 | Length → ft
1-1/4" | 32 | 1.38 | 1.442 | [6 empty] | 100 | Pressure → psi
1-1/2" | 40 | 1.61 | 1.682 | [6 empty] | 150 | Velocity: display ← ft/s
2" | 50 | 2.067 | 2.157 | [6 empty] | 200
2-1/2" | 65 | 2.469 | 2.635 | [6 empty] | 250 | Water static head (psi/ft) | 0.433
3" | 80 | 3.068 | 3.26 | [6 empty] | 300
4" | 100 | 4.026 | 4.26 | [6 empty] | 400
5" | 125 | 5.047 | 5.295 | [6 empty] | 450
6" | 150 | 6.065 | 6.357 | [6 empty] | 500
8" | 200 | 7.981 | 8.329 | [6 empty] | 750
10" | 250 | 10.02 | 10.42 | [6 empty] | 1000
12" | 300 | 11.938 | 12.39 | [6 empty] | 1250
1500
2000
2500
Equivalent length of fittings (ft), Schedule 40 steel, C=120 (commonly published NFPA 13 values; blank = not listed) | [9 empty] | 3000
Nominal | DN | 90° elbow (std) | 90° elbow (long) | 45° elbow | Tee (run) | Tee/cross (branch) | Gate valve | Butterfly valve | Swing check | 3500
1" | 25 | 2 | 1 | 1 | 1 | 5 |  |  | 5 | 4000
1-1/4" | 32 | 3 | 2 | 1 | 1 | 6 |  |  | 7 | 4500
1-1/2" | 40 | 4 | 2 | 2 | 2 | 8 | 1 |  | 9 | 5000
2" | 50 | 5 | 3 | 2 | 4 | 10 | 1 | 6 | 11
2-1/2" | 65 | 6 | 4 | 3 | 5 | 12 | 1 | 7 | 14
3" | 80 | 7 | 5 | 3 | 5 | 15 | 1 | 10 | 16
4" | 100 | 10 | 6 | 4 | 6 | 20 | 2 | 12 | 22
5" | 125 | 12 | 8 | 5 | 8 | 25 | 2 | 9 | 27
6" | 150 | 14 | 9 | 7 | 10 | 30 | 3 | 10 | 32
8" | 200 | 18 | 13 | 9 | 12 | 35 | 4 | 12 | 45
10" | 250 | 22 | 16 | 11 | 15 | 50 | 5 | 15 | 55
12" | 300 | 27 | 18 | 13 | 18 | 60 | 6 | 18 | 65