## Heat Load Calculator
BuildMEP Free Heat Load Calculator
Room-by-room cooling load estimate (sensible + latent) — SI units. Fill in the yellow cells.
Preliminary single-room estimate. Verify project weather, envelope data and the required calculation method before final design or equipment selection.
This offline calculator uses standard simplified cooling-load formulas and is independent from BuildMEP's live web calculator — the two are not guaranteed to return identical results, since each uses its own internal assumptions.
1. Project / Location
Project or room reference | Office - Level 2 - Room 201
Location | Doha, Qatar
Space use | Office
2. Room Geometry
Room length | 6 | m
Room width | 5 | m
Clear (ceiling) height | 3 | m
Floor area (calculated) | 30 | m²
Room volume (calculated) | 90 | m³
3. Indoor and Outdoor Design Conditions
| Dry bulb (°C) | RH (%)
Indoor design condition | 24 | 50
Outdoor design condition | 46 | 30
Design temperature difference (calculated) | 22 | K
4. Envelope: Construction / Exposure
Orientation | Net wall (m²) | Glazing (m²) | Solar factor (W/m²)
North | 0 | 0 | 120
East | 0 | 0 | 90
South | 15 | 3 | 240
West | 9 | 6 | 550
Wall U-value | 0.35 | W/m²·K
Glass U-value | 2.8 | W/m²·K
Glass SHGC | 0.35
Shading multiplier (1.0 = unshaded) | 0.75
Roof U-value (0 if roof not exposed) | 0.3 | W/m²·K
External door area | 0 | m²
Door U-value | 2 | W/m²·K
5. Internal Loads: People, Lighting, Equipment
Number of people | 6
Sensible heat per person | 75 | W/person
Latent heat per person | 55 | W/person
Occupancy / diversity factor (0-1) | 1
Lighting load density | 10 | W/m²
Equipment load density | 8 | W/m²
6. Outdoor Air: Ventilation and Infiltration
Ventilation air flow | 180 | L/s
Infiltration rate | 0.5 | ACH
Inputs valid
Results
Envelope conduction (walls, roof, doors) | 382.8 | W
Glazing conduction | 554.4 | W
Glazing solar gain | 1055.25 | W
People — sensible | 450 | W
People — latent | 330 | W
Lighting | 300 | W
Equipment | 240 | W
Ventilation — sensible | 4870.8 | W
Infiltration air flow (calculated) | 12.5 | L/s
Infiltration — sensible | 338.25 | W
Humidity ratio check (kg water / kg dry air)
|  |  |  | Outdoor humidity ratio | 0.019147
|  |  |  | Indoor humidity ratio | 0.0092955
Ventilation + infiltration — latent | 5708.0462 | W
Totals
Total sensible load | 8.1915 | kW
Total latent load | 6.038 | kW
TOTAL COOLING LOAD | 14.2295 | kW
Total cooling load in Tons of Refrigeration | 4.0459 | TR
Sensible heat ratio (SHR) | 0.57567
Load density (calculated) | 474.3182 | W/m²
Safety / allowance margin | 10%
RECOMMENDED NOMINAL CAPACITY | 4.5 | TR
Preliminary estimate only. Nominal capacity includes the selected allowance and 0.5 TR rounding.
Method: steady-state envelope conduction (U x area x indoor/outdoor dry-bulb difference), fixed orientation glazing-solar allowances, internal gains and outdoor air. Sensible outdoor-air load uses 1.23 x L/s x dry-bulb difference. Humidity ratios are estimated from dry bulb and RH at a fixed 101.325 kPa pressure; latent load uses 3010 x combined L/s x humidity-ratio difference. Negative outdoor-air components represent signed offsets; no positive net load means zero nominal capacity. The formula-domain checks do not validate temperature/pressure applicability. This tool does not implement hourly thermal storage, coincidence, Heat Balance, RTS or CLTD/CLF tables. Use an approved project method and check equipment performance before selection.
Input-validation revision: 15 October 2026. Online tool: https://buildmep.com/free-heat-load-calculator/ — independent assumptions; results may differ.