## About
BuildMEP — Thrust Block Design Calculator
Sizing for concrete thrust blocks at pipe bends, tees/wyes, and dead ends on buried water & fire mains — buildmep.com
How to use this workbook
1. Open the “Bend (Angle)” tab for bends/elbows, or the “Tee, Wye & Dead End” tab for branch fittings, tees, and capped/dead ends.
2. Fill in the yellow input cells only — pipe outside diameter (OD), design/test pressure, deflection angle (bends only), soil type, depth of cover, safety factor, and minimum block thickness.
3. Results (thrust force, required bearing area, minimum concrete volume) calculate automatically.
4. See the “Soil Bearing Reference” tab for the built-in soil table — use a project-specific geotechnical value instead wherever one is available.
Method
Bends: T = 2 × P × A × sin(Δ/2)
Tees, wyes, dead ends, caps, valves: T = P × A
Required bearing area: A_required = (T ÷ q_allow) × Safety Factor
Minimum concrete volume: V = A_required × minimum block thickness
T = resultant thrust force (lb) · P = internal design/test pressure (psi) · A = pipe cross-sectional area based on actual OD (in²) · Δ = fitting deflection angle (°) · q_allow = allowable soil bearing pressure (lb/ft²)
Disclaimer
Preliminary sizing only, based on the standard thrust-force method used across most municipal and utility water design standards, and the USDA-NRCS National Engineering Handbook (Part 636, Chapter 52, Table 52-6) reference soil bearing values. This is a starting point for preliminary design — it is not a substitute for a project-specific geotechnical report, your governing design standard, or a licensed engineer's review before finalizing concrete dimensions on a real job. The thrust block must bear against undisturbed soil; backfilled or previously excavated ground does not have the bearing capacity the reference table assumes.
buildmep.com · free MEP engineering tools & guides

## Bend (Angle)
Thrust Block — Bend / Angle
Inputs
| Deflection angle, Δ (degrees) | 90 | °
| Pipe outside diameter, D (in) | 11.1 | in
| Design / test pressure, P (psi) | 150 | psi
| Safety factor, SF | 1.5
| Minimum block thickness (in) | 8 | in
| Soil type | Dense fine to coarse sand
| Depth of cover to block center (ft) | 4
| — or enter a site-specific q_allow (lb/ft²) directly: |  | lb/ft² (leave blank to use the soil table)
Results
Pipe cross-sectional area, A (in²)
Thrust force, T (lb)
Allowable soil bearing pressure, q_allow (lb/ft²)
Required bearing area (ft²)
Minimum concrete volume (ft³)
Minimum concrete volume (cu yd)
The block must bear against undisturbed soil — this table does not apply to backfilled or previously excavated ground. Preliminary sizing only; confirm against a project-specific geotechnical report and your governing design standard before finalizing dimensions.

## Tee, Wye & Dead End
Thrust Block — Tee, Wye & Dead End
Inputs
| Pipe outside diameter, D (in) | 11.1 | in
| Design / test pressure, P (psi) | 150 | psi
| Safety factor, SF | 1.5
| Minimum block thickness (in) | 8 | in
| Soil type | Dense fine to coarse sand
| Depth of cover to block center (ft) | 4
| — or enter a site-specific q_allow (lb/ft²) directly: |  | lb/ft² (leave blank to use the soil table)
Results
Pipe cross-sectional area, A (in²)
Thrust force, T (lb)
Allowable soil bearing pressure, q_allow (lb/ft²)
Required bearing area (ft²)
Minimum concrete volume (ft³)
Minimum concrete volume (cu yd)
The block must bear against undisturbed soil — this table does not apply to backfilled or previously excavated ground. Preliminary sizing only; confirm against a project-specific geotechnical report and your governing design standard before finalizing dimensions.

## Soil Bearing Reference
Allowable Soil Bearing Pressure — Reference Table
Source: USDA-NRCS National Engineering Handbook, Part 636, Chapter 52, Table 52-6. Reference values for undisturbed natural soil — use a site-specific geotechnical value instead wherever one is available.
| Natural soil material | 2 ft | 3 ft | 4 ft | 5 ft
| Sound bedrock | 8000 | 10000 | 10000 | 10000
| Dense sand and gravel mixture (θ≈40°) | 1200 | 1800 | 2400 | 3000
| Dense fine to coarse sand (θ≈35°) | 800 | 1200 | 1650 | 2100
| Silt and clay mixture (θ≈25°) | 500 | 700 | 950 | 1200
Values in lb/ft², depth = distance from grade to the center of the thrust block.